## Sheet1
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
ATA Technologies Corporation
Raw Wastewater |  |  | After Prefilter (5 micron) |  | After GAC Column |  | After 1st Media Column |  | Final | Total
Sample 1 | Sample 2 | Average | Conc. | Removal | Conc. | Removal | Conc. | Removal | Effluent | Removal
41.3 | 33 | 37.15 | 12.4 | 66.62% | 9.72 | 21.61% | 0.425 | 95.63% | 0.112 | 99.7%
|  |  | Notes: | 1. Data in ug/l (ppb) unless otherwise noted.
2. Raw wastewater test sample collected 2/21/97.
3. Concentration Data from analytical reports
of the MWRA Central Laboratory.