## Sheet1
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
ICET, Inc.
RUN # 1
| Raw Wastewater |  |  | After Column 1 |  | After Column 2
Test # | Sample 1 | Sample 2 | Average | Conc. | Removal | Conc. | Removal | Total Removal
1 | 16.8 | 17.1 | 16.95 | 4.09 | 0.7587 | 0.415 | 0.89853 | 0.97552
2 | " | " | 16.95 | 3.54 | 0.79115 | 1.36 | 0.61582 | 0.91976
3 | " | " | 16.95 | 3.87 | 0.77168 | 2.16 | 0.44186 | 0.87257
4 | " | " | 16.95 | 6 | 0.64602 | 2.42 | 0.59667 | 0.85723
5 | " | " | 16.95 | 6.6 | 0.61062 | 2.78 | 0.57879 | 0.83599
6 | " | " | 16.95 | 6.45 | 0.61947 | 3.62 | 0.43876 | 0.78643
7 | " | " | 16.95 | 6.3 | 0.62832 | 3.72 | 0.40952 | 0.78053
8 | " | " | 16.95 | 8.9 | 0.47493 | 3.8 | 0.57303 | 0.77581
9 | " | " | 16.95 | 8.75 | 0.48378 | 4.01 | 0.54171 | 0.76342
10 | " | " | 16.95 | 8.2 | 0.51622 | 4.68 | 0.42927 | 0.72389
11 | " | " | 16.95 | 7.8 | 0.53982 | 4.7 | 0.39744 | 0.72271
12 | " | " | 16.95 | 9.15 | 0.46018 | 4.8 | 0.47541 | 0.71681
| Notes: | 1. Data in ug/L (ppb) unless otherwise specified.
2. Raw wastewater test sample collected 5/23/97.
3. Concentration data from analytical reports of the MWRA Central Laboratory.

## Sheet2
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
ICET, Inc.
RUN #2
| Raw Wastewater |  |  | After Column 1 |  | After Column 2
Test # | Sample 1 | Sample 2 | Average | Conc. | Removal | Conc. | Removal | Total Removal
1 | 16.8 | 17.1 | 16.95 | 0.39 | 0.97699 | 0.845 | -1.1667 | 0.95015
2 | " | " | 16.95 | 1.76 | 0.89617 | 0.28 | 0.84091 | 0.98348
3 | " | " | 16.95 | 2.13 | 0.87434 | 1.11 | 0.47887 | 0.93451
4 | " | " | 16.95 | 2.74 | 0.83835 | 1.7 | 0.37956 | 0.89971
5 | " | " | 16.95 | 3.19 | 0.8118 | 2.2 | 0.31034 | 0.87021
6 | " | " | 16.95 | 3.4 | 0.79941 | 2.38 | 0.3 | 0.85959
7 | " | " | 16.95 | 3.69 | 0.7823 | 2.37 | 0.35772 | 0.86018
8 | " | " | 16.95 | 3.73 | 0.77994 | 2.36 | 0.36729 | 0.86077
9 | " | " | 16.95 | 3.86 | 0.77227 | 2.85 | 0.26166 | 0.83186
10 | " | " | 16.95 | 3.78 | 0.77699 | 3.09 | 0.18254 | 0.8177
11 | " | " | 16.95 | 4.53 | 0.73274 | 3.43 | 0.24283 | 0.79764
12 | " | " | 16.95 | 4.53 | 0.73274 | 3.34 | 0.26269 | 0.80295
| Notes: | 1. Data in ug/L (ppb) unless otherwise specified.
2. Raw wastewater test sample collected 5/23/97.
3. Concentration data from analytical reports of the MWRA Central Laoboratory.

## Sheet3
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
ICET, Inc.
RUN #3
| Raw Wastewater |  |  | After Column 1 |  | After Column 2
Test # | Sample 1 | Sample 2 | Average | Conc. | Removal | Conc. | Removal | Total Removal
1 | 16.4 | 12.8 | 14.6 | 4.2 | 0.71233 | 1.85 | 0.55952 | 0.87329
2 | " | " | 14.6 | 4.27 | 0.70753 | 3.79 | 0.11241 | 0.74041
3 | " | " | 14.6 | 3.04 | 0.79178 | 4.41 | -0.45066 | 0.69795
4 | " | " | 14.6 | 2.01 | 0.86233 | 3.02 | -0.50249 | 0.79315
5 | " | " | 14.6 | 1.28 | 0.91233 | 2.08 | -0.625 | 0.85753
6 | " | " | 14.6 | 0.876 | 0.94 | 1.13 | -0.28995 | 0.9226
| Notes: | 1. Data in ug/L (ppb) unless otherwise specified.
2. Raw wastewater test sample collected 5/23/97.
3. Concentration data from analytical reports of the MWRA Central Laboratory.

## Sheet4
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
ICET, Inc.
RUN #4
| Raw Wastewater |  |  | After Column 1 |  | After Column 2
Test # | Sample 1 | Sample 2 | Average | Conc. | Removal | Conc. | Removal | Total Removal
1 | 16.4 | 12.8 | 14.6 | 3.73 | 0.74452 | 0.1 | 0.97319 | 0.99315
2 | " | " | 14.6 | 5.4 | 0.63014 | 3.67 | 0.32037 | 0.74863
3 | " | " | 14.6 | 4.27 | 0.70753 | 4.47 | -0.046838 | 0.69384
4 | " | " | 14.6 | 2.07 | 0.85822 | 2.19 | -0.057971 | 0.85
5 | " | " | 14.6 | 1.12 | 0.92329 | 1.67 | -0.49107 | 0.88562
6 | " | " | 14.6 | 1.03 | 0.92945 | 0.754 | 0.26796 | 0.94836
| Notes: | 1. Data in ug/L (ppb) unless otherwise specified.
2. Raw wastewater test sample collected 5/23/97.
3. Concentration data from analytical reports of the MWRA Central Laboratory.