## Sheet1
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
KDF Fluid Treatment, Inc.
| Raw Wastewater |  | After 20 micron Filter |  | After Absorbent Column |  | After Column 2 |  | Total
Sample 1 | Sample 2 | Average | Conc. | Removal | Conc. | Removal | Conc. | Removal | Removal
41.3 | 33 | 37.15 | 22.9 | 38.36% | 25.8 | -12.66% | 18.4 | 28.68% | 50.47%
41.3 | 33 | 37.15 | 28.2 | 24.09% | 26.9 | 4.61% | 20.2 | 24.91% | 45.63%
| Notes: | 1. Data in ug/l (ppb) unless otherwise specified.
2. Raw wastewater test sample collected 2/21/97.
3. Concentration data from analytical reports of the MWRA Central Laboratory.