## Sheet1
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Mercury Test Data and Removals
Soils N.V.
MWRA Central Laboratory Data
[5 empty] | Raw Wastewater |  |  | After Electrolysis
|  | Component | Trial | Sample | Sample | Average | Effluent |  | Total
|  |  | # | 1 | 2 |  |  |  | Removal
|  | Mercury | 1 | 24.9 | 21.8 | 23.35 |  | 2.14 | 0.90835
|  | Mercury | 2 | 24.9 | 21.8 | 23.35 | < | 0.2 | 0.99143
|  | Mercury | 3 | 24.9 | 21.8 | 23.35 |  | 0.508 | 0.97824
|  | Mercury | 4 | 24.9 | 21.8 | 23.35 | < | 0.2 | 0.99143
|  | Mercury | 5 | 24.9 | 21.8 | 23.35 |  | 0.26 | 0.98887
|  | Mercury | 6 | 24.9 | 21.8 | 23.35 | < | 0.2 | 0.99143
|  | Mercury | 7 | 24.9 | 21.8 | 23.35 | < | 0.2 | 0.99143
|  | Mercury | 8 | 24.9 | 21.8 | 23.35 | < | 0.2 | 0.99143
Soils N.V. Data
|  |  |  | Raw Wastewater |  |  |  |  | After Electrolysis
Component | Trial | Sample | Sample | Sample | Sample | Sample | Average |  | Effluent | Total
| # | 1 | 2 | 3 | 4 | 5 |  |  |  | Removal
Mercury | 1 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 2.1 | 0.84559
Mercury | 2 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 3.6 | 0.73529
Mercury | 3 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 1.5 | 0.88971
Mercury | 4 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 0.8 | 0.94118
Mercury | 5 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 1.2 | 0.91176
Mercury | 6 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 4.9 | 0.63971
Mercury | 7 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 2.5 | 0.81618
Mercury | 8 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 5 | 0.63235
[7 empty] | Averages : |  | 2.7 | 0.80147
| Notes: | 1. All values are reported in ug/l (ppb) unless otherwise noted.
2. Raw wastewater test sample was collected 3/28/97.
3. Differences in analytical data of the MWRA Central Laboratory and Soils N.V. may
be the result of mercury evaporation from samples during trans-Atlantic flights.
4. Because the Soils N.V. data was obtained from consistent samples, the Subgroup
Report uses the Soils N.V. mercury test data and associated removals.

## Sheet2
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Priority Pollutant Metals (Non-Hg) Test Data
Soils N.V.
|  | Raw Wastewater |  |  |  |  | Raw Wastewater | [10 empty] | Electrolysis Effluent
Component |  | Sample |  |  | Sample |  | Sample |  | Average |  | Trial |  | Trial |  | Trial |  | Trial |  | Trial |  | Trial |  | Trial |  | Trial
|  | 1 |  |  | 1 |  | 2 |  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
SILVER |  | 335 |  |  | 335 |  | 325 |  | 330 |  | 31.2 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2
ARSENIC | < | 25 | < | < | 25 | < | 25 | < | 25 |  | 1080 | < | 50 | < | 50 | < | 50 | < | 50 | < | 50 | < | 50 | < | 50
BERYLLIUM | < | 1 | < | < | 1 | < | 1 | < | 1 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2 | < | 2
CADMIUM | < | 2 | < | < | 2 | < | 2 | < | 2 | < | 8 | < | 8 | < | 8 |  | 10.8 | < | 8 |  | 17.8 |  | 23.2 |  | 15.8
CHROMIUM |  | 81.2 |  |  | 81.2 |  | 74.9 |  | 78.05 |  | 12 | < | 4 |  | 18.4 |  | 28.8 |  | 25.5 |  | 35 |  | 42.2 |  | 34.8
COPPER |  | 386 |  |  | 386 |  | 376 |  | 381 |  | 214 |  | 104 |  | 283 |  | 134 |  | 177 |  | 95.5 |  | 224 |  | 189
NICKEL |  | 7 |  |  | 7 |  | 5.2 |  | 6.1 |  | 30.2 |  | 50.6 |  | 54.6 |  | 132 |  | 116 |  | 152 |  | 190 |  | 145
LEAD |  | 170 |  |  | 170 |  | 163 |  | 166.5 | < | 24 | < | 24 | < | 60 | < | 60 | < | 60 | < | 60 |  | 75.9 | < | 60
ANTIMONY | < | 25 | < | < | 25 | < | 25 | < | 25 | < | 50 | < | 50 |  | 69.4 |  | 73.2 | < | 50 |  | 141 |  | 151 |  | 83
SELENIUM |  | 36.6 | < |  | 36.6 | < | 30 | < | 33.3 | < | 60 | < | 2.2 | < | 2.2 | < | 2.2 | < | 2.2 | < | 2.2 | < | 2.2 | < | 2.2
THALLIUM | < | 35 | < | < | 35 | < | 35 | < | 35 | < | 70 | < | 70 | < | 140 | < | 140 | < | 140 | < | 140 | < | 140 | < | 140
ZINC |  | 56.4 |  |  | 56.4 |  | 45.8 |  | 51.1 |  | 36 |  | 148 |  | 177 |  | 175 |  | 136 |  | 250 |  | 230 |  | 224
[9 empty] | Notes: |  | 1. Data in ug/L (ppb) unless otherwise specified.
2. Raw wastewater test sample collected 3/28/97.
3. Data from analytical reports of the MWRA Central Laboratory.
4. Varying detection limits resulted from dilutions used to address
analytical interferences in samples.
|  | Sample |  |  |  |  | Sample
|  | 1 |  |  |  |  | 2
|  | 335 |  |  |  |  | 325
| < | 25 | < |  |  |  | 25
| < | 1 | < |  |  |  | 1
| < | 2 | < |  |  |  | 2
|  | 81.2 |  |  |  |  | 74.9
|  | 386 |  |  |  |  | 376
|  | 7 |  |  |  |  | 5.2
|  | 170 |  |  |  |  | 163
| < | 25 | < |  |  |  | 25
|  | 36.6 | < |  |  |  | 30
| < | 35 | < |  |  |  | 35
|  | 56.4 |  |  |  |  | 45.8
Component
SILVER
ARSENIC
BERYLLIUM
CADMIUM
CHROMIUM
COPPER
NICKEL
LEAD
ANTIMONY
SELENIUM
THALLIUM
ZINC
Note: All values are reported in ug/L (ppb) unless otherwise specified.
Raw Wastewater
|  |  | Sample |  |  |  |  | Sample
|  |  | 1 |  |  |  |  | 2
|  |  | 335 |  |  |  |  | 325
|  | < | 25 |  |  |  | < | 25
|  | < | 1 |  |  |  | < | 1
|  | < | 2 |  |  |  | < | 2
|  |  | 81.2 |  |  |  |  | 74.9
|  |  | 386 |  |  |  |  | 376
|  |  | 7 |  |  |  |  | 5.2
|  |  | 170 |  |  |  |  | 163
|  | < | 25 |  |  |  | < | 25
|  |  | 36.6 |  |  |  | < | 30
|  | < | 35 |  |  |  | < | 35
|  |  | 56.4 |  |  |  |  | 45.8

## Sheet3
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1

## Sheet4
Comparison of Mercury Data from Soils N.V. and MWRA
INFLUENT | MWRA | Soils N.V. | Effluent | MWRA | Soils N.V.
Influent 1 | 24.9 | 17.6 | Effluent 1 | 2.14 | 2.1
Influent 2 | 21.8 | 12.3 | Effluent 2 | 0.2 | 3.6
Influent 3 | *** | 10.8 | Effluent 3 | 0.508 | 1.5
Influent 4 | *** | 13.4 | Effluent 4 | 0.2 | 4
Influent 5 | *** | 13.8 | Effluent 5 | 0.2 | 0.8
Average | 23.35 | 13.58 | Effluent 6 | 0.2 | 1.2
|  |  | Effluent 7 | 0.2 | 4.9
|  |  | Effluent 8 | 0.2 | 2.5
Note: Data collected 3/28/97
: All values are measured in UG/L unless otherwise specified

## Sheet5
EFFLUENT
| MWRA |  |  | SOILS N.V.
Component | 1 | 2 | AVERAGE | 1 | 2 | 3 | 4 | 5 | AVERAGE
Mercury
| MWRA | [7 empty] | SOILS N.V.
Component | EFF 1 | EFF 2 | EFF 3 | EFF 4 | EFF 5 | EFF 6 | EFF 7 | EFF 8 | EFF 1 | EFF 2 | EFF 3 | EFF 4 | EFF 5 | EFF 6 | EFF 7 | EFF 8
Mercury | 2.14 | 0.2 | 0.508 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.1 | 3.6 | 1.5 | 4 | 0.8 | 1.2 | 4.9 | 2.5