## Sheet1
MWRA/MASCO Mercury Work Group - Technology Identification Subgroup
Bench-Scale Feasibility Testing Project
Comparison of MWRA Central Laboratory and Soils N.V. Mercury Data
MWRA Central Laboratory Data
[5 empty] | Raw Wastewater |  | After Electrolysis
|  | Component | Trial | Sample | Sample | Average | Effluent
|  |  | # | 1 | 2
|  | Mercury | 1 | 24.9 | 21.8 | 23.35 |  | 2.14
|  | Mercury | 2 | " | " | " | < | 0.2
|  | Mercury | 3 | " | " | " |  | 0.508
|  | Mercury | 4 | " | " | " | < | 0.2
|  | Mercury | 5 | " | " | " |  | 0.26
|  | Mercury | 6 | " | " | " | < | 0.2
|  | Mercury | 7 | " | " | " | < | 0.2
|  | Mercury | 8 | " | " | " | < | 0.2
Soils N.V. Data
|  |  |  | Raw Wastewater |  |  |  | After Electrolysis
Component | Trial | Sample | Sample | Sample | Sample | Sample | Average | Effluent
| # | 1 | 2 | 3 | 4 | 5
Mercury | 1 | 17.6 | 12.3 | 10.8 | 13.4 | 13.8 | 13.6 |  | 2.1
Mercury | 2 | " | " | " | " | " | " |  | 3.6
Mercury | 3 | " | " | " | " | " | " |  | 1.5
Mercury | 4 | " | " | " | " | " | " |  | 0.8
Mercury | 5 | " | " | " | " | " | " |  | 1.2
Mercury | 6 | " | " | " | " | " | " |  | 4.9
Mercury | 7 | " | " | " | " | " | " |  | 2.5
Mercury | 8 | " | " | " | " | " | " |  | 5
Notes: | 1. Data in ug/l (ppb) unless otherwise noted.
2. Raw wastewater test sample collected 3/28/97.
3. The differences in analytical data of the MWRA Central Laboratory and Soils N.V. may have been
the result of mercury evaporation from samples during East-bound (raw wastewater) and West-
bound (effluent) trans-Atlantic flights.
4. Because the Soils N.V. analytical data were from samples that were not subject to overseas
shipment, the Subgroup Report used the Soils N.V. mercury test data and associated removals.

## Sheet2
MWRA/MASCO Mercury Work Group; Technology Identification Subgroup
MWRA Results of Soils N.V. Feasibilty Test
|  |  |  | Raw Wastewater |  |  | Influent |  | Trial 1 |  | Trial 2 |  | Influent |  | Trial 3 |  | Trial 4
| Component |  |  | Sample |  | Sample |  | Average |  | conc |  | conc |  | Average |  | conc |  | conc
|  |  |  | 1 |  | 2 |  |  |  | ppb |  | ppb |  |  |  | ppb |  | ppb
| SILVER |  |  | 335 |  | 325 |  | 330 |  | 31.2 | < | 2 |  | 330 | < | 2 | < | 2
| ARSENIC |  | < | 25 | < | 25 | < | 25 |  | 1080 | < | 50 | < | 25 | < | 50 | < | 50
| BERYLLIUM |  | < | 1 | < | 1 | < | 1 | < | 2 | < | 2 | < | 1 | < | 2 | < | 2
| CADMIUM |  | < | 2 | < | 2 | < | 2 | < | 8 | < | 8 | < | 2 | < | 8 |  | 10.8
| CHROMIUM |  |  | 81.2 |  | 74.9 |  | 78.05 |  | 12 | < | 4 |  | 78.05 |  | 18.4 |  | 28.8
| COPPER |  |  | 386 |  | 376 |  | 381 |  | 214 |  | 104 |  | 381 |  | 283 |  | 134
| NICKEL |  |  | 7 |  | 5.2 |  | 6.1 |  | 30.2 |  | 50.6 |  | 6.1 |  | 54.6 |  | 132
| LEAD |  |  | 170 |  | 163 |  | 166.5 | < | 24 | < | 24 |  | 166.5 | < | 60 | < | 60
| ANTIMONY |  | < | 25 | < | 25 | < | 25 | < | 50 | < | 50 | < | 25 |  | 69.4 |  | 73.2
| SELENIUM |  |  | 36.6 | < | 30 | < | 33.3 | < | 60 | < | 2.2 | < | 33.3 | < | 2.2 | < | 2.2
| THALLIUM |  | < | 35 | < | 35 | < | 35 | < | 70 | < | 70 | < | 35 | < | 140 | < | 140
| ZINC |  |  | 56.4 |  | 45.8 |  | 51.1 |  | 36 |  | 148 |  | 51.1 |  | 177 |  | 175
|  |  |  | Raw Wastewater |  |  | Influent |  | Trial 5 |  | Trial 6 |  | Influent |  | Trial 7 |  | Trial 8
| Component |  |  | Sample |  | Sample |  | Average |  | conc |  | conc |  | Average |  | conc |  | conc
|  |  |  | 1 |  | 2 |  |  |  | ppb |  | ppb |  |  |  | ppb |  | ppb
| SILVER |  |  | 335 |  | 325 |  | 330 | < | 2 | < | 2 |  | 330 | < | 2 | < | 2
| ARSENIC |  | < | 25 | < | 25 | < | 25 | < | 50 | < | 50 | < | 25 | < | 50 | < | 50
| BERYLLIUM |  | < | 1 | < | 1 | < | 1 | < | 2 | < | 2 | < | 1 | < | 2 | < | 2
| CADMIUM |  | < | 2 | < | 2 | < | 2 | < | 8 |  | 17.8 | < | 2 |  | 23.2 |  | 15.8
| CHROMIUM |  |  | 81.2 |  | 74.9 |  | 78.05 |  | 25.5 |  | 35 |  | 78.05 |  | 42.2 |  | 34.8
| COPPER |  |  | 386 |  | 376 |  | 381 |  | 177 |  | 95.5 |  | 381 |  | 224 |  | 189
| NICKEL |  |  | 7 |  | 5.2 |  | 6.1 |  | 116 |  | 152 |  | 6.1 |  | 190 |  | 145
| LEAD |  |  | 170 |  | 163 |  | 166.5 | < | 60 | < | 60 |  | 166.5 |  | 75.9 | < | 60
| ANTIMONY |  | < | 25 | < | 25 | < | 25 | < | 50 |  | 141 | < | 25 |  | 151 |  | 83
| SELENIUM |  |  | 36.6 | < | 30 | < | 33.3 | < | 2.2 | < | 2.2 | < | 33.3 | < | 2.2 | < | 2.2
| THALLIUM |  | < | 35 | < | 35 | < | 35 | < | 140 | < | 140 | < | 35 | < | 140 | < | 140
| ZINC |  |  | 56.4 |  | 45.8 |  | 51.1 |  | 136 |  | 250 |  | 51.1 |  | 230 |  | 224
| Note: 1. All values are reported in ug/L (ppb) unless otherwise specified. |  |  | Raw Wastewater
2. MWRA Data Collected 3/28/97
|  |  |  | Sample |  | Sample
|  |  |  | 1 |  | 2
|  |  |  | 335 |  | 325
|  |  | < | 25 | < | 25
|  |  | < | 1 | < | 1
|  |  | < | 2 | < | 2
|  |  |  | 81.2 |  | 74.9
|  |  |  | 386 |  | 376
|  |  |  | 7 |  | 5.2
|  |  |  | 170 |  | 163
|  |  | < | 25 | < | 25
|  |  |  | 36.6 | < | 30
|  |  | < | 35 | < | 35
|  |  |  | 56.4 |  | 45.8
|  | Component | [5 empty] | Component
|  | SILVER | [5 empty] | SILVER
|  | ARSENIC | [5 empty] | ARSENIC
|  | BERYLLIUM | [5 empty] | BERYLLIUM
|  | CADMIUM | [5 empty] | CADMIUM
|  | CHROMIUM | [5 empty] | CHROMIUM
|  | COPPER | [5 empty] | COPPER
|  | NICKEL | [5 empty] | NICKEL
|  | LEAD | [5 empty] | LEAD
|  | ANTIMONY | [5 empty] | ANTIMONY
|  | SELENIUM | [5 empty] | SELENIUM
|  | THALLIUM | [5 empty] | THALLIUM
|  | ZINC | [5 empty] | ZINC
Note: All values are reported in ug/L (ppb) unless otherwise specified.
Raw Wastewater
[5 empty] | Sample |  | Sample
[5 empty] | 1 |  | 2
[5 empty] | 335 |  | 325
|  |  |  | < | 25 | < | 25
|  |  |  | < | 1 | < | 1
|  |  |  | < | 2 | < | 2
[5 empty] | 81.2 |  | 74.9
[5 empty] | 386 |  | 376
[5 empty] | 7 |  | 5.2
[5 empty] | 170 |  | 163
|  |  |  | < | 25 | < | 25
[5 empty] | 36.6 | < | 30
|  |  |  | < | 35 | < | 35
[5 empty] | 56.4 |  | 45.8

## Sheet3
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1
Component |  | Raw 1 |  | Raw 2 |  | Avg Raw
|  | Waste |  | Waste |  | Waste
Silver |  | 335 |  | 325 |  | 330
Arsenic | < | 25 | < | 25 | < | 25
Beryllium | < | 1 | < | 1 | < | 1
Cadmium | < | 2 | < | 2 | < | 2
Chromium |  | 81.2 |  | 74.9 |  | 78.05
Copper |  | 386 |  | 376 |  | 381
Nickel |  | 7 |  | 5.2 |  | 6.1
Lead |  | 170 |  | 163 |  | 166.5
Antimony | < | 25 | < | 25 | < | 25
Selenium |  | 36.6 | < | 30 | < | 33.3
Thallium | < | 35 | < | 35 | < | 35
Zinc |  | 56.4 |  | 45.8 |  | 51.1

## Sheet4
Comparison of Mercury Data from Soils N.V. and MWRA
INFLUENT | MWRA | Soils N.V. | Effluent | MWRA | Soils N.V.
Influent 1 | 24.9 | 17.6 | Effluent 1 | 2.14 | 2.1
Influent 2 | 21.8 | 12.3 | Effluent 2 | 0.2 | 3.6
Influent 3 | *** | 10.8 | Effluent 3 | 0.508 | 1.5
Influent 4 | *** | 13.4 | Effluent 4 | 0.2 | 4
Influent 5 | *** | 13.8 | Effluent 5 | 0.2 | 0.8
Average | 23.35 | 13.58 | Effluent 6 | 0.2 | 1.2
|  |  | Effluent 7 | 0.2 | 4.9
|  |  | Effluent 8 | 0.2 | 2.5
Note: Data collected 3/28/97
: All values are measured in UG/L unless otherwise specified

## Sheet5
EFFLUENT
| MWRA |  |  | SOILS N.V.
Component | 1 | 2 | AVERAGE | 1 | 2 | 3 | 4 | 5 | AVERAGE
Mercury
| MWRA | [7 empty] | SOILS N.V.
Component | EFF 1 | EFF 2 | EFF 3 | EFF 4 | EFF 5 | EFF 6 | EFF 7 | EFF 8 | EFF 1 | EFF 2 | EFF 3 | EFF 4 | EFF 5 | EFF 6 | EFF 7 | EFF 8
Mercury | 2.14 | 0.2 | 0.508 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 2.1 | 3.6 | 1.5 | 4 | 0.8 | 1.2 | 4.9 | 2.5